## Data_Dictionary
Column name in dataset | Short name | Variable type | Unit | Description | Values / range | Notes
Polymeric Insulator Sample Number | Sample | Identifier | - | Identifier of the polymeric insulator sample. | 1, 2, 3, 4 (A, B, C, D) | Used to distinguish the four polymeric insulator samples included in the dataset.
Creepage Distance (CD) (cm) | CD | Geometry variable | cm | Total creepage/leakage distance along the surface of the insulator between end-fittings. | Sample-specific | Represents the surface distance along the insulator profile.
Arcing Distance (AD) (cm) | AD | Geometry variable | cm | Shortest air-gap distance between the higher and grounded end-fittings. | Sample-specific | Represents the direct electrical clearance between the two end-fittings.
Creepage factor (CD/AD) | CF | Geometry variable | - | Ratio of creepage distance to arcing distance. | Calculated as CD/AD | Calculated from the creepage distance and arcing distance columns.
Relative Humidity (%) | RH | Environmental condition | % | Relative humidity condition during the laboratory experiment. | 65, 70, 80, 90 | Relative humidity was applied using cold ultrasonic humidification in a controlled environmental chamber.
Accelerated Aging (day) | Aging | Environmental condition | Day | Accelerated ageing duration or ageing level of the polymeric insulator sample. | 0, 15, 30, 45 | The insulator samples were aged under multi-stress ageing conditions in a chamber. [Combination of electrical stress, heat, and UV-C radiation]
J (non-uniformity Pollution Degree) | J | Environmental condition | - | Non-uniformity pollution degree/index representing unevenness of the severity of leeward and windward pollution on the insulator surface. | 1, 1.5, 3, 6, 9, 15 | Defined according to fan-shaped non-uniform pollution condition.
K (Occupation Ratio) (%) | K | Environmental condition | % | Occupation ratio associated with the fan-shaped non-uniform pollution distribution condition associated with the leeward and windward side surface of the insulator. | 0, 15, 20, 30, 40, 50 | Represents the percentage occupation ratio used in the fan-shaped non-uniform pollution condition.
Salt Deposit Density (SDD) (mg/cm^2) | SDD | Environmental condition | mg/cm^2 | Salt deposit density representing the pollution severity on the insulator surface. | 0.03, 0.06, 0.10, 0.14 | Reported as salt deposit density for the tested condition.
Flashover Voltage (kV) | FOV | Measured result | kV | Flashover voltage measured for the corresponding sample and test condition. | Dataset-specific measured values | Main measured result provided in the dataset. [Average of 5 FOV experiments. Increasing voltage rate was 2 kV/s]

## Citation_Licence
Field | Entry
Dataset title | Flashover Voltage Dataset for Polymeric Insulators under Environmental Conditions
Repository | Mendeley Data
Version | 1.0
Licence | CC0 1.0 Universal
Suggested citation | Citation of this dataset is optional; however, users who wish to cite the dataset may use the citation details generated by Mendeley Data after publication. [LPA Science Inc, Elshan Ahani]. (2026). Flashover Voltage Dataset for Polymeric Insulators under Environmental Conditions. Mendeley Data, Version 1.0. DOI: https://github.com/LPA-Science/Flashover.
Email address | info@lpa.co.ir lpa.sci.inc@gmail.com
NOTE: | The column definitions apply to the Whole samples sheet, which contains the combined data for all four polymeric insulator samples.